Here’s an example of when I would use a “Time of Day” object block in a complex Win-911 notification policy.

Alarm: 1.00 inches of rain in an hour

Purpose: Alarm is used to identify when samples need to be taken and when a report needs to be generated

Frequency: Contact list only needs to know if the alarm is active once in a given day (midnight to midnight) so the alarm should not trigger multiple notifications in one day.

Notification policy:

- Alarm active – send notification to contact list

- Alarm changes to inactive once rain stops

- Delay until midnight

- Auto-acknowledge alarm at midnight so that alarm changes to terminal

- Alarm will be ready to re-activate the next day if needed

This alarm could become active at any time of the day so I can’t use delay blocks to time the auto-acknowledge at midnight.